## Betjening og totaludskrift
Statisk undertryk for sugearm ø 76 mm
| 0 grader = ligeud |  | Vælg [0,1,2 eller 3] og kanal-længde i m | Flow [m3/h] | Samlet tryktab [Pa]
| Antal af drejeled, 0 grader: |  | 1 | 0 | 0
| Antal af drejeled, 45 grader: |  | 1 | 20 | 7.5522
| Antal af drejeled, 90 grader: |  | 1 | 30 | 14.3897
| Antal af drejeled, 135 grader: |  | 0 | 45 | 28.4729
| Antal af drejeled, 165 grader: |  | 0 | 60 | 47.1482
| Antal m lige 76 mm alu kanal: |  | 2.2 | 75 | 70.4158
| DATO: |  | 14/9 2015 | 90 | 98.2755
|  |  |  | 105 | 130.7274
|  |  |  | 120 | 167.7715
|  |  |  | 135 | 209.4078
|  |  |  | 150 | 255.6363
|  |  |  | 165 | 306.457
|  |  |  | 180 | 361.8699
|  |  |  | 195 | 421.8749
|  |  |  | 210 | 486.4722
|  |  |  | 225 | 555.6616
|  |  |  | 240 | 629.4433
|  |  |  | 255 | 707.8171
|  |  |  | 270 | 790.7831
|  |  |  | 285 | 878.3413
|  |  |  | 300 | 970.4917
Overskriftsgenerator: |  | Permavent 14/9 2015, 1 stk ligeud + 1 stk 45 grader + 1 stk 90 grader + 0 stk 135 grader + 0 stk 165 grader + 2,2 meter 76mm kanal
Firmanavn: |  | Permavent

## Sheet1 (hidden)
| C:\Users\Kim\Desktop\[O76-tryktabsberegner.xlsx]Betjening og totaludskrift | [17 empty] | Pressure loss in pipe | mathmatical velocity
[18 empty] | 0 | 0 | 0
| Name: | James Rosenfeldt | [6 empty] | inner diameter[m] | 0.055 | [7 empty] | 10 | 0.50954 | 1.1692
| Measuring devices: | [16 empty] | 20 | 1.7743 | 2.3384
| date: | 2015-09-18 | [15 empty] | 30 | 3.6813 | 3.5075
[18 empty] | 40 | 6.1786 | 4.6767
| 1 joint of 0 degrees |  |  |  | , |  |  |  |  | 1 joint of 135 degrees | [7 empty] | 50 | 9.2327 | 5.8459
| flow rate m^3/h | m^3 | time[s] | pressure loss [Pa] | hz | mathmatical pressure loss in pipe [Pa/m] | flow rate[m^3/s] | velocity[m/s] |  | flow rate m^3/h | m^3 | time | pressure loss | hz | mathmatical pressure loss in pipe[Pa/m] | flow rate[m^3/s] | velocity[m/s] | 60 | 12.819 | 7.0151
1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 16.9184 | 8.1843
2 | 23.6066 | 0.4 | 61 | 12.5 | 10 | 2.3913 | 23.6066 | 2.76 | 2 | 29.3878 | 0.4 | 49 | 24.6 | 10 | 3.5472 | 29.3878 | 3.436 | 80 | 21.5151 | 9.3535
3 | 45.7143 | 0.8 | 63 | 41.2 | 15 | 7.8573 | 45.7143 | 5.3448 | 3 | 47.7108 | 1.1 | 83 | 63.6 | 15 | 8.4858 | 47.7108 | 5.5783 | 90 | 26.5961 | 10.5226
4 | 69.2308 | 1 | 52 | 91.1 | 20 | 16.5852 | 69.2308 | 8.0943 | 4 | 65.9542 | 1.2 | 65.5 | 124.3 | 20 | 15.1991 | 65.9542 | 7.7112 | 100 | 32.1501 | 11.6918
5 | 87.8049 | 1.5 | 61.5 | 144.3 | 25 | 25.4399 | 87.8049 | 10.266 | 5 | 83.4783 | 1.6 | 69 | 191.7 | 25 | 23.2281 | 83.4783 | 9.7601 | 110 | 38.1671 | 12.861
6 | 104.9007 | 2.2 | 75.5 | 211.8 | 30 | 35.0415 | 104.9007 | 12.2648 | 6 | 100.4651 | 1.8 | 64.5 | 275.1 | 30 | 32.4197 | 100.4651 | 11.7462 | 120 | 44.6384 | 14.0302
7 | 122.7663 | 2.5 | 73.31 | 279.5 | 35 | 46.5077 | 122.7663 | 14.3536 | 7 | 117.1525 | 2.4 | 73.75 | 367.6 | 35 | 42.7499 | 117.1525 | 13.6973 | 130 | 51.5561 | 15.1994
8 | 131.7073 | 3 | 82 | 322.5 | 37.5 | 52.7813 | 131.7073 | 15.399 | 8 | 134.6763 | 2.6 | 69.5 | 476.8 | 40 | 54.9422 | 134.6763 | 15.7461 | 140 | 58.9132 | 16.3686
[18 empty] | 150 | 66.7031 | 17.5377
| 1 joint of 45 degrees | [8 empty] | 1 joint of 165 degrees | [7 empty] | 160 | 74.92 | 18.7069
| flow rate m^3/h | m^3 | time | pressure loss | hz | mathmatical pressure loss in pipe [Pa/m] | flow rate[m^3/s] | velocity[m/s] |  | flow rate m^3/h | m^3 | time | pressure loss | hz | mathmatical pressure loss in pipe [Pa/m] | flow rate[m^3/s] | velocity[m/s] | 170 | 83.5584 | 19.8761
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 92.6131 | 21.0453
2 | 24 | 0.35 | 52.5 | 14.3 | 10 | 2.4636 | 24 | 2.806 | 2 | 29.6907 | 0.4 | 48.5 | 26.3 | 10 | 3.6133 | 29.6907 | 3.4714 | 190 | 102.0795 | 22.2145
3 | 46.2857 | 0.9 | 70 | 44.5 | 15 | 8.035 | 46.2857 | 5.4116 | 3 | 48 | 0.6 | 45 | 68.1 | 15 | 8.5786 | 48 | 5.6121 | 200 | 111.9531 | 23.3836
4 | 67.2897 | 1 | 53.5 | 88.7 | 20 | 15.7576 | 67.2897 | 7.8674 | 4 | 65.8537 | 0.9 | 49.2 | 128.6 | 20 | 15.1574 | 65.8537 | 7.6995
5 | 86.1972 | 1.7 | 71 | 143 | 25 | 24.6076 | 86.1972 | 10.078 | 5 | 83.0769 | 1.5 | 65 | 203 | 25 | 23.0275 | 83.0769 | 9.7132
6 | 104.3478 | 2 | 69 | 205 | 30 | 34.7098 | 104.3478 | 12.2002 | 6 | 100.1325 | 2.1 | 75.5 | 283.5 | 30 | 32.2268 | 100.1325 | 11.7073
7 | 122.0339 | 3 | 88.5 | 280 | 35 | 46.0094 | 122.0339 | 14.268 | 7 | 116.8831 | 2.5 | 77 | 387.4 | 35 | 42.5731 | 116.8831 | 13.6658
8 | 130.9091 | 3 | 82.5 | 323 | 37.5 | 52.2069 | 130.9091 | 15.3057 | 8 | 132.6781 | 3 | 81.4 | 505.6 | 40 | 53.4836 | 132.6781 | 15.5125
1 joint of 90 degrees
| flow rate m^3/h | m^3 | time | pressure loss | hz | mathmatical pressure loss in pipe[Pa/m] | flow rate[m^3/h] | velocity[m/s]
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27.6923 | 0.5 | 65 | 18.1 | 10 | 3.1873 | 27.6923 | 3.2377
3 | 47.6471 | 0.9 | 68 | 52.6 | 15 | 8.4654 | 47.6471 | 5.5708
4 | 66.6667 | 1.25 | 67.5 | 99.5 | 20 | 15.4959 | 66.6667 | 7.7945
5 | 85.0394 | 1.5 | 63.5 | 158.3 | 25 | 24.0159 | 85.0394 | 9.9427
6 | 102.8571 | 2 | 70 | 234.8 | 30 | 33.8224 | 102.8571 | 12.0259
7 | 120 | 2.3 | 69 | 322.9 | 35 | 44.6384 | 120 | 14.0302
8 | 129.0323 | 2.5 | 69.75 | 366.2 | 37.5 | 50.8673 | 129.0323 | 15.0862
The pressure loss through the joint is equal to the difference between the Total pressure loss-pressure loss through aluminium pipe

## Sheet2 (2) (hidden)
Pressure loss extrapolation to 200 [m^3/h] | [9 empty] | aluminium pipe pressure loss per meter
[21 empty] | Tryktab i drejeled alene | [10 empty] | overskrift | Permavent 13 Marts 2013 0 stk ligeud + 2 stk 45grader + 1 stk 90grader + 0 stk 135grader + 0 stk 165grader
Total 0 degrees |  | Total 45 degrees |  | Total 90 degrees |  | Total 135 degrees |  | Total 165 degrees |  | Pipe 0 degrees |  | Pipe 45 degrees |  | Pipe 90 degrees |  | Pipe 135 degrees |  |  | Pipe 165 degrees |  | Joint 0 degrees |  | Joint 45 degrees |  | Joint 90 degrees |  | Joint 135 degrees |  |  | Joint 165 degrees |  | trykvalgskema
Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] |  | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] |  | Flow rate[m^3/h] | Pressure loss in joint[Pa] | 0 grader = ligeud | vælg [0,1,2 eller 3] | flow m3/h | samlet tryktab [Pa]
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Antal af drejeled, 0 grader: | 0 | 0 | 0
10 | 2.9735 | 10 | 2.6858 | 10 | 2.5285 | 10 | 4.6576 | 10 | 3.614 | 10 | 0.82729 | 10 | 0.82399 | 10 | 0.81892 | 10 | 0.83418 | 0.00261842x2 + 0.05723342x | 10 | 0.82897 | 10 | 2.1462 | 10 | 1.8618 | 10 | 1.7095 | 10 | 3.8234 | 0.00261842x2 + 0.05723342x | 10 | 2.785 | Antal af drejeled, 45 grader: | 2 | 10 | 11.2148
20 | 9.5186 | 20 | 8.9597 | 20 | 9.4308 | 20 | 14.2797 | 20 | 12.8093 | 20 | 2.1799 | 20 | 2.174 | 20 | 2.1653 | 20 | 2.192 |  | 20 | 2.183 | 20 | 7.3387 | 20 | 6.7857 | 20 | 7.2654 | 20 | 12.0876 |  | 20 | 10.6263 | Antal af drejeled, 90 grader: | 1 | 20 | 39.4379
30 | 19.6352 | 30 | 18.8216 | 30 | 20.7069 | 30 | 28.8662 | 30 | 27.586 | 30 | 4.0578 | 30 | 4.0501 | 30 | 4.0392 | 30 | 4.0736 |  | 30 | 4.0621 | 30 | 15.5774 | 30 | 14.7715 | 30 | 16.6677 | 30 | 24.7926 |  | 30 | 23.5239 | Antal af drejeled, 135 grader: | 0 | 30 | 84.6694
40 | 33.3233 | 40 | 32.2715 | 40 | 36.357 | 40 | 48.4172 | 40 | 47.944 | 40 | 6.461 | 40 | 6.4523 | 40 | 6.4405 | 40 | 6.4788 |  | 40 | 6.4662 | 40 | 26.8623 | 40 | 25.8192 | 40 | 29.9164 | 40 | 41.9384 |  | 40 | 41.4778 | Antal af drejeled, 165 grader: | 0 | 40 | 146.9094
50 | 50.583 | 50 | 49.3095 | 50 | 56.3808 | 50 | 72.9327 | 50 | 73.8833 | 50 | 9.3895 | 50 | 9.3805 | 50 | 9.3694 | 50 | 9.4077 |  | 50 | 9.3954 | 50 | 41.1936 | 50 | 39.929 | 50 | 47.0115 | 50 | 63.525 |  | 50 | 64.4879 | antal m lige 55 mm alu kanal | 1.8 | 50 | 226.1577
60 | 71.4143 | 60 | 69.9356 | 60 | 80.7786 | 60 | 102.4127 | 60 | 105.404 | 60 | 12.8433 | 60 | 12.8348 | 60 | 12.8257 | 60 | 12.8603 |  | 60 | 12.8496 | 60 | 58.571 | 60 | 57.1008 | 60 | 67.9529 | 60 | 89.5523 |  | 60 | 92.5543 |  |  | 60 | 322.4144
70 | 95.8171 | 70 | 94.1496 | 70 | 109.5502 | 70 | 136.8571 | 70 | 142.506 | 70 | 16.8224 | 70 | 16.8151 | 70 | 16.8095 | 70 | 16.8366 |  | 70 | 16.8289 | 70 | 78.9947 | 70 | 77.3345 | 70 | 92.7407 | 70 | 120.0205 |  | 70 | 125.6771 |  |  | 70 | 435.6795
80 | 123.7915 | 80 | 121.9517 | 80 | 142.6956 | 80 | 176.266 | 80 | 185.1894 | 80 | 21.3268 | 80 | 21.3215 | 80 | 21.3207 | 80 | 21.3366 |  | 80 | 21.3333 | 80 | 102.4647 | 80 | 100.6302 | 80 | 121.3749 | 80 | 154.9294 |  | 80 | 163.8561 |  |  | 80 | 565.953
90 | 155.3374 | 90 | 153.3419 | 90 | 180.2149 | 90 | 220.6393 | 90 | 233.454 | 90 | 26.3565 | 90 | 26.354 | 90 | 26.3594 | 90 | 26.3602 |  | 90 | 26.3627 | 90 | 128.9809 | 90 | 126.9879 | 90 | 153.8555 | 90 | 194.2791 |  | 90 | 207.0913 |  |  | 90 | 713.2348
100 | 190.4548 | 100 | 188.3201 | 100 | 222.1081 | 100 | 269.9772 | 100 | 287.3001 | 100 | 31.9115 | 100 | 31.9125 | 100 | 31.9257 | 100 | 31.9075 |  | 100 | 31.9172 | 100 | 158.5433 | 100 | 156.4076 | 100 | 190.1825 | 100 | 238.0696 |  | 100 | 255.3829 |  |  | 100 | 877.5251
110 | 229.1439 | 110 | 226.8863 | 110 | 268.3752 | 110 | 324.2795 | 110 | 346.7274 | 110 | 37.9918 | 110 | 37.997 | 110 | 38.0193 | 110 | 37.9786 |  | 110 | 37.9967 | 110 | 191.152 | 110 | 188.8893 | 110 | 230.3558 | 110 | 286.3009 |  | 110 | 308.7308 |  |  | 110 | 1058.8238
120 | 271.4044 | 120 | 269.0406 | 120 | 319.016 | 120 | 383.5462 | 120 | 411.7361 | 120 | 44.5975 | 120 | 44.6077 | 120 | 44.6405 | 120 | 44.5733 |  | 120 | 44.6012 | 120 | 226.8069 | 120 | 224.433 | 120 | 274.3755 | 120 | 338.973 |  | 120 | 367.1349 |  |  | 120 | 1257.1308
130 | 317.2365 | 130 | 314.7829 | 130 | 374.0308 | 130 | 447.7775 | 130 | 482.3262 | 130 | 51.7284 | 130 | 51.7443 | 130 | 51.7891 | 130 | 51.6916 |  | 130 | 51.7309 | 130 | 265.5081 | 130 | 263.0386 | 130 | 322.2417 | 130 | 396.0858 |  | 130 | 430.5953 |  |  | 130 | 1472.4462
140 | 366.6402 | 140 | 364.1133 | 140 | 433.4194 | 140 | 516.9732 | 140 | 558.4976 | 140 | 59.3846 | 140 | 59.4071 | 140 | 59.4652 | 140 | 59.3337 |  | 140 | 59.3855 | 140 | 307.2556 | 140 | 304.7062 | 140 | 373.9542 | 140 | 457.6395 |  | 140 | 499.112 |  |  | 140 | 1704.7701
150 | 419.6154 | 150 | 417.0317 | 150 | 497.1819 | 150 | 591.1334 | 150 | 640.2503 | 150 | 67.5661 | 150 | 67.5959 | 150 | 67.6688 | 150 | 67.4995 |  | 150 | 67.5653 | 150 | 352.0493 | 150 | 349.4359 | 150 | 429.513 | 150 | 523.6339 |  | 150 | 572.685 |  |  | 150 | 1954.1023
160 | 476.1621 | 160 | 473.5382 | 160 | 565.3182 | 160 | 670.258 | 160 | 727.5843 | 160 | 76.2729 | 160 | 76.3107 | 160 | 76.3999 | 160 | 76.1889 |  | 160 | 76.27 | 160 | 399.8892 | 160 | 397.2274 | 160 | 488.9183 | 160 | 594.0691 |  | 160 | 651.3143 |  |  | 160 | 2220.4429
170 | 536.2805 | 170 | 533.6327 | 170 | 637.8284 | 170 | 754.3471 | 170 | 820.4997 | 170 | 85.5051 | 170 | 85.5516 | 170 | 85.6584 | 170 | 85.402 |  | 170 | 85.4999 | 170 | 450.7754 | 170 | 448.081 | 170 | 552.1699 | 170 | 668.9451 |  | 170 | 734.9999 |  |  | 170 | 2503.7919
180 | 599.9703 | 180 | 597.3152 | 180 | 714.7124 | 180 | 843.4007 | 180 | 918.9965 | 180 | 95.2625 | 180 | 95.3186 | 180 | 95.4445 | 180 | 95.1388 |  | 180 | 95.2548 | 180 | 504.7078 | 180 | 501.9966 | 180 | 619.2679 | 180 | 748.2619 |  | 180 | 823.7417 |  |  | 180 | 2804.1493
190 | 667.2317 | 190 | 664.5858 | 190 | 795.9703 | 190 | 937.4188 | 190 | 1023.0745 | 190 | 105.5452 | 190 | 105.6116 | 190 | 105.7579 | 190 | 105.3993 |  | 190 | 105.5347 | 190 | 561.6865 | 190 | 558.9741 | 190 | 690.2124 | 190 | 832.0195 |  | 190 | 917.5398 |  |  | 190 | 3121.515
200 | 738.0647 | 200 | 735.4444 | 200 | 881.602 | 200 | 1036.4013 | 200 | 1132.7339 | 200 | 116.3533 | 200 | 116.4307 | 200 | 116.5989 | 200 | 116.1835 |  | 200 | 116.3397 | 200 | 621.7114 | 200 | 619.0137 | 200 | 765.0031 | 200 | 920.2178 |  | 200 | 1016.3942 |  |  | 200 | 3455.8892

## Sheet2 (hidden)
Pressure loss extrapolation to 200 [m^3/h] | [9 empty] | aluminium pipe pressure loss per meter
Tryktab i drejeled alene
Total 0 degrees |  | Total 45 degrees |  | Total 90 degrees |  | Total 135 degrees |  | Total 165 degrees |  | Pipe 0 degrees |  | Pipe 45 degrees |  | Pipe 90 degrees |  | Pipe 135 degrees |  |  | Pipe 165 degrees |  | Joint 0 degrees |  | Joint 45 degrees |  | Joint 90 degrees |  | Joint 135 degrees |  |  | Joint 165 degrees
Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Total pressure loss[Pa] |  | Flow rate[m^3/h] | Total pressure loss[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] | Flow rate[m^3/h] | Pressure loss in joint[Pa] |  | Flow rate[m^3/h] | Pressure loss in joint[Pa]
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
10 | 2.9735 | 10 | 2.6858 | 10 | 2.5285 | 10 | 4.6576 | 10 | 3.614 | 10 | 0.82729 | 10 | 0.82399 | 10 | 0.81892 | 10 | 0.83418 | 0.00261842x2 + 0.05723342x | 10 | 0.82897 | 10 | 2.1462 | 10 | 1.8618 | 10 | 1.7095 | 10 | 3.8234 | 0.00261842x2 + 0.05723342x | 10 | 2.785
20 | 9.5186 | 20 | 8.9597 | 20 | 9.4308 | 20 | 14.2797 | 20 | 12.8093 | 20 | 2.1799 | 20 | 2.174 | 20 | 2.1653 | 20 | 2.192 |  | 20 | 2.183 | 20 | 7.3387 | 20 | 6.7857 | 20 | 7.2654 | 20 | 12.0876 |  | 20 | 10.6263
30 | 19.6352 | 30 | 18.8216 | 30 | 20.7069 | 30 | 28.8662 | 30 | 27.586 | 30 | 4.0578 | 30 | 4.0501 | 30 | 4.0392 | 30 | 4.0736 |  | 30 | 4.0621 | 30 | 15.5774 | 30 | 14.7715 | 30 | 16.6677 | 30 | 24.7926 |  | 30 | 23.5239
40 | 33.3233 | 40 | 32.2715 | 40 | 36.357 | 40 | 48.4172 | 40 | 47.944 | 40 | 6.461 | 40 | 6.4523 | 40 | 6.4405 | 40 | 6.4788 |  | 40 | 6.4662 | 40 | 26.8623 | 40 | 25.8192 | 40 | 29.9164 | 40 | 41.9384 |  | 40 | 41.4778
50 | 50.583 | 50 | 49.3095 | 50 | 56.3808 | 50 | 72.9327 | 50 | 73.8833 | 50 | 9.3895 | 50 | 9.3805 | 50 | 9.3694 | 50 | 9.4077 |  | 50 | 9.3954 | 50 | 41.1936 | 50 | 39.929 | 50 | 47.0115 | 50 | 63.525 |  | 50 | 64.4879
60 | 71.4143 | 60 | 69.9356 | 60 | 80.7786 | 60 | 102.4127 | 60 | 105.404 | 60 | 12.8433 | 60 | 12.8348 | 60 | 12.8257 | 60 | 12.8603 |  | 60 | 12.8496 | 60 | 58.571 | 60 | 57.1008 | 60 | 67.9529 | 60 | 89.5523 |  | 60 | 92.5543
70 | 95.8171 | 70 | 94.1496 | 70 | 109.5502 | 70 | 136.8571 | 70 | 142.506 | 70 | 16.8224 | 70 | 16.8151 | 70 | 16.8095 | 70 | 16.8366 |  | 70 | 16.8289 | 70 | 78.9947 | 70 | 77.3345 | 70 | 92.7407 | 70 | 120.0205 |  | 70 | 125.6771
80 | 123.7915 | 80 | 121.9517 | 80 | 142.6956 | 80 | 176.266 | 80 | 185.1894 | 80 | 21.3268 | 80 | 21.3215 | 80 | 21.3207 | 80 | 21.3366 |  | 80 | 21.3333 | 80 | 102.4647 | 80 | 100.6302 | 80 | 121.3749 | 80 | 154.9294 |  | 80 | 163.8561
90 | 155.3374 | 90 | 153.3419 | 90 | 180.2149 | 90 | 220.6393 | 90 | 233.454 | 90 | 26.3565 | 90 | 26.354 | 90 | 26.3594 | 90 | 26.3602 |  | 90 | 26.3627 | 90 | 128.9809 | 90 | 126.9879 | 90 | 153.8555 | 90 | 194.2791 |  | 90 | 207.0913
100 | 190.4548 | 100 | 188.3201 | 100 | 222.1081 | 100 | 269.9772 | 100 | 287.3001 | 100 | 31.9115 | 100 | 31.9125 | 100 | 31.9257 | 100 | 31.9075 |  | 100 | 31.9172 | 100 | 158.5433 | 100 | 156.4076 | 100 | 190.1825 | 100 | 238.0696 |  | 100 | 255.3829
110 | 229.1439 | 110 | 226.8863 | 110 | 268.3752 | 110 | 324.2795 | 110 | 346.7274 | 110 | 37.9918 | 110 | 37.997 | 110 | 38.0193 | 110 | 37.9786 |  | 110 | 37.9967 | 110 | 191.152 | 110 | 188.8893 | 110 | 230.3558 | 110 | 286.3009 |  | 110 | 308.7308
120 | 271.4044 | 120 | 269.0406 | 120 | 319.016 | 120 | 383.5462 | 120 | 411.7361 | 120 | 44.5975 | 120 | 44.6077 | 120 | 44.6405 | 120 | 44.5733 |  | 120 | 44.6012 | 120 | 226.8069 | 120 | 224.433 | 120 | 274.3755 | 120 | 338.973 |  | 120 | 367.1349
130 | 317.2365 | 130 | 314.7829 | 130 | 374.0308 | 130 | 447.7775 | 130 | 482.3262 | 130 | 51.7284 | 130 | 51.7443 | 130 | 51.7891 | 130 | 51.6916 |  | 130 | 51.7309 | 130 | 265.5081 | 130 | 263.0386 | 130 | 322.2417 | 130 | 396.0858 |  | 130 | 430.5953
140 | 366.6402 | 140 | 364.1133 | 140 | 433.4194 | 140 | 516.9732 | 140 | 558.4976 | 140 | 59.3846 | 140 | 59.4071 | 140 | 59.4652 | 140 | 59.3337 |  | 140 | 59.3855 | 140 | 307.2556 | 140 | 304.7062 | 140 | 373.9542 | 140 | 457.6395 |  | 140 | 499.112
150 | 419.6154 | 150 | 417.0317 | 150 | 497.1819 | 150 | 591.1334 | 150 | 640.2503 | 150 | 67.5661 | 150 | 67.5959 | 150 | 67.6688 | 150 | 67.4995 |  | 150 | 67.5653 | 150 | 352.0493 | 150 | 349.4359 | 150 | 429.513 | 150 | 523.6339 |  | 150 | 572.685
160 | 476.1621 | 160 | 473.5382 | 160 | 565.3182 | 160 | 670.258 | 160 | 727.5843 | 160 | 76.2729 | 160 | 76.3107 | 160 | 76.3999 | 160 | 76.1889 |  | 160 | 76.27 | 160 | 399.8892 | 160 | 397.2274 | 160 | 488.9183 | 160 | 594.0691 |  | 160 | 651.3143
170 | 536.2805 | 170 | 533.6327 | 170 | 637.8284 | 170 | 754.3471 | 170 | 820.4997 | 170 | 85.5051 | 170 | 85.5516 | 170 | 85.6584 | 170 | 85.402 |  | 170 | 85.4999 | 170 | 450.7754 | 170 | 448.081 | 170 | 552.1699 | 170 | 668.9451 |  | 170 | 734.9999
180 | 599.9703 | 180 | 597.3152 | 180 | 714.7124 | 180 | 843.4007 | 180 | 918.9965 | 180 | 95.2625 | 180 | 95.3186 | 180 | 95.4445 | 180 | 95.1388 |  | 180 | 95.2548 | 180 | 504.7078 | 180 | 501.9966 | 180 | 619.2679 | 180 | 748.2619 |  | 180 | 823.7417
190 | 667.2317 | 190 | 664.5858 | 190 | 795.9703 | 190 | 937.4188 | 190 | 1023.0745 | 190 | 105.5452 | 190 | 105.6116 | 190 | 105.7579 | 190 | 105.3993 |  | 190 | 105.5347 | 190 | 561.6865 | 190 | 558.9741 | 190 | 690.2124 | 190 | 832.0195 |  | 190 | 917.5398
200 | 738.0647 | 200 | 735.4444 | 200 | 881.602 | 200 | 1036.4013 | 200 | 1132.7339 | 200 | 116.3533 | 200 | 116.4307 | 200 | 116.5989 | 200 | 116.1835 |  | 200 | 116.3397 | 200 | 621.7114 | 200 | 619.0137 | 200 | 765.0031 | 200 | 920.2178 |  | 200 | 1016.3942